## AQUAFIX
calculation sheet for
separator systems for light liquids according to EN 858
project:
client:
architect:
basis |  |  |  |  | to fill in
class 1/class 2 separator systems
separator systems for light liquds, oil and petrol
Areas of application
Separator systems are used in a wide variety of situations to
fulfill a number of different requirements. It is important to establish
why a separator system is needed an what specific function it is
expected to fulfill before selecting the appropriate size and type of
installation.
[5 empty] | Application of separator system | [5 empty] | a
| Areas of application |  |  |  | (a, b oder c)
to treast waste water (trade effluent) from industrial processes,
(a) | vehicle washing, cleansing of oil covered parts or other sources,
e. g. petrol station forecourts
to treat contaminated rainwater (run-off) from impervious areas,
(b) | e. g. car parks, roads, factory yard areas
to retain any spillage of light liquid and to protect the
(c) | surrounding area
Components of separator systems
A separator system may consist of several components.
Annex B of the norm shows how to select these components.
[5 empty] | Select the system's configuration | [7 empty] | 2
Rainwater
For category b uses, the size of the separator will depend on the |  |  |  |  | uncovered wash place: | [5 empty] | 0 | m²
design, rainfall intensity and the catchment area draining to the separator. |  |  |  |  | uncovered area for oil spreaded vehicles: | [6 empty] | m²
Qr = Y x i x A |  |  |  |  | uncovered area for damaged vehicles: | [6 empty] | m²
i is the rainfall intensity, in l/s ha |  |  |  |  | uncovered area for the filling up of vehicles: | [6 empty] | m²
A is the area receiving rainfall, measured horzontally, in ha |  |  |  |  | other areas: | [6 empty] | m²
Y is the dimensionless run-off coefficient | [11 empty] | m²
The rainfall intensity i mainly depends on the analysis of local rainfall | [8 empty] | area receiving rainfall A: |  | 0 | m²
data and shall be adopted according to local regulations. |  |  |  |  | selected i |  |  |  | l/(s x ha) |  | 0 | ha
Surface areas covered by a canapy will receive reduced rainfall.
For the purpose of equation the value A may be reduced for these |  |  |  |  | selected Y:
areas.
[5 empty] | Qr = x l/(s x ha) x 0 ha |  |  |  |  | = | 0 | l/s
Waste water
arising from work processes
Qva = valve draw-off coefficient in l/s.
number | Nominal diameter
of | 15 | 20 | 25
(thread)
points | R 1/2 | R 3/4
flow from draw-off pipes
1 | 0.5 | 1 | 1.7 |  | Qs1 = |  | pce |  | DN25 | = | 0 | l/s |  | 1 | 0.5 | 1 | 1.7
2 | 0.5 | 1 | 1.7 |  |  | 0 | pce |  | DN20 | = | 0 | l/s |  | 2 | 0.5 | 1 | 1.7
3 | 0.35 | 0.7 | 1.2 |  | 0 |  | pce |  | DN15 | = | 0 | l/s |  | 3 | 0.35 | 0.7 | 1.2
4 | 0.25 | 0.5 | 0.85 |  | 0 |  |  |  | sum Qs1 | = | 0 | l/s |  | 4 | 0.25 | 0.5 | 0.85
5 | 0.1 | 0.2 | 0.3 |  | (max. 5 per DN) | [8 empty] | 5 | 0.1 | 0.2 | 0.3
values given for supply pressure of about 4 to 5 bar | [13 empty] | 6 | 0.1 | 0.2 | 0.3
[14 empty] | 7 | 0.1 | 0.2 | 0.3
In case of supply pressure differing from that stated above | [13 empty] | 8 | 0.1 | 0.2 | 0.3
the following formula shall be used. | [13 empty] | 9 | 0.1 | 0.2 | 0.3
[14 empty] | 10 | 0.1 | 0.2 | 0.3
Qs1(x bar) = Qs1 (4 bar)/SQR (4 bar/ X bar)) |  |  |  |  | supply pressure in bar: | [8 empty] | 11 | 0.1 | 0.2 | 0.3
[14 empty] | 12 | 0.1 | 0.2 | 0.3
[5 empty] | corrected sum Qs1 | [5 empty] | #DIV/0! | l/s |  | 13 | 0.1 | 0.2 | 0.3
[14 empty] | 14 | 0.1 | 0.2 | 0.3
Qs2 = | flow from car washes |  |  |  | Qs2 = | 0 | pcs | automatic |  | = | 0 | l/s |  | 15 | 0.1 | 0.2 | 0.3
[8 empty] | car washes | [5 empty] | 1000 | 0 | 0 | 0
Qs2 = | 2 | per wash place/drive through
(back pressure >20 bar)
Waste water from low pressure car washes with a
back pressure up to 20 bar does usually not contain
any significant amount of liquid.
Qs3 = | flow from high pressure cleaning units |  |  |  | Qs3 = |  | pcs | high pressure |  | = | 0 | l/s | 1000 | 0 | 1000 | 0 | 1000 | 0
[8 empty] | cleaning units |  |  |  |  | 1000 | 0 | 1000 | 0 | 1000 | 0
Qs3 = | 2 | for the 1. unit | [10 empty] | 1000 | 0 | 1000 | 0 | 1000 | 0
Qs3 = | 1 | for each following unit | [10 empty] | 1000 | 0 | 1000 | 0 | 1000 | 0
Qs3 = | 1 | for the 1. unit, when used together | [10 empty] | 1000 | 0 | 1000 | 0 | 1000 | 0
|  | with an automatic car wash | [11 empty] | 0 |  | 0 |  | 0
These values have to be applicated independently from the actual
water consumtion of the units.
Faeces do not have to be discharged into the separator.
Qs = Qs1 + Qs2 + Qs3 |  |  |  |  | Qs = 00 l/s + 00 l/s + 00 l/s |  |  |  |  | = | #DIV/0! | l/s
impediment factor f x
discharge type |  | f x |  |  | impediment factor f x |  |  |  |  | = | 2 |  | a | 2
a) |  | 2 | [10 empty] | b | 1 |  | TRUE
b) |  | not relevant as Qs=0 (only rainwater) | [10 empty] | c | 1
c) |  | 1
density factor f d | [12 empty] | 0.1 | 1
density (g/cm3) | up to 0,85 | over 0,85 up to 0,90 | over 0,90 up to 0,95 | [9 empty] | 0.86 | 1.5
| density factor f d | [11 empty] | 0.91 | 2
[5 empty] | density of the | [7 empty] | 0
S-II-P | 1 | 2 | 3 |  | light liquids |  |  |  | g/cm³ |  |  |  | 0.1
S-I-P | 1 | 1.5 | 2 | [9 empty] | 1.6 | 1 | 1 | 2 | 3 | 0
S-II-I-P | 1 | 1 | 1 | [9 empty] | 3.1 | 2 | 1 | 1.5 | 2 | 0
[5 empty] | density factor f d |  |  |  |  | = | #N/A |  | 6.1 | 3 | 1 | 1 | 1 | 0
[14 empty] | 4 | 1 | 2 | 3 | 0
Do future factory enlagements, |  |  |  |  | security addition rainwater | [6 empty] | l/s |  | 5 | 1 | 1.5 | 2 | 0
more units have to be considered? |  |  |  |  | security addition waste water | [6 empty] | l/s
[5 empty] | security addition sum | [5 empty] | 0 | l/s | 0.01 | 3
Determinaton of the separator's size | [12 empty] | 3.1 | 4
NS = ( Qr + f x x Qs ) x f d |  |  |  |  | calculated size |  |  |  |  | = | #DIV/0! |  | 4.01 | 6
[5 empty] | nominal size NS |  |  |  |  | = | #DIV/0! |  | 6.01 | 8
Note: | [12 empty] | 8.01 | 10
When a separator is not expected to receive rainwater and waste- |  |  |  |  | NS out of Qr |  |  |  |  | = | 0 |  | 10.01 | 15
water at the same time, then the separator can be sized separately |  |  |  |  | NS out of Qs |  |  |  |  | = | 0 |  | 15.01 | 20
for rainwater and wastewater. |  |  |  |  | decisive NS at separation |  |  |  |  | = | 0 |  | 20.01 | 30
The biggest calculated size is then decisive. |  |  |  |  | Is there a separation ? ( yes / no ) | [7 empty] | 30.01 | 40
[13 empty] | 40.01 | 50
[13 empty] | 50.01 | 65
[5 empty] | chosen size NS | [7 empty] | 60.01 | 75
[5 empty] | (to fill in) | [7 empty] | 75.01 | 80
Oil sludge trap | [12 empty] | 80.01 | 100 | #DIV/0!
[13 empty] | 100.01 | 120
classification | Quantity of sludge anticipated |  | sludge trap |  | classification of oil sludge | [7 empty] | 120.01 | 130
| for e. g. |  | volume |  | (1-4) | [7 empty] | 130.01 | 140
none | condensate |  | 0 |  | 0 | [7 empty] | 140.01 | 150
(1) |  |  |  |  | #DIV/0! | [7 empty] | 150.01 | 160
small | processing waste water with defined |  | 100 * NS / f d | [9 empty] | 160.01 | 170
(2) | small sludge volume, all rainwater |  | (a) |  | calculated sludge trap volume | [5 empty] | #N/A | l | 170.01 | 180
| collecting areas where a small amount | [11 empty] | 180.01 | 200
| of silt from traffic or similar appears, i. e. | [11 empty] | 200.01 | 250
| catchment basins on petrol tank areas | [11 empty] | 250.01 | 300
| and covered filling stations | [11 empty] | 300.01 | 400
[13 empty] | 400.01 | 500
medium | filling stations, carwash by hand, part |  | 200 * NS / f d |  | selected sludge trap volume: | [6 empty] | l | 500.01 | 600
(3) | washing, bus washing places, |  | (b) |  | (to fill in) | [7 empty] | 600.01 | 700
| waste water from garages, vehicle parking | [11 empty] | 700.01 | 800
| lots, power plants, machinery plants | [11 empty] | 800.01 | 900
[13 empty] | 900.01 | 1000
[13 empty] | 1000.01 | >1000
high | washing plants for site vehicles, site |  | 300 * NS / f d
(4) | machines, farm machines, truck wash |  | (b)
| places | [11 empty] | 1 | 0 |  | #DIV/0! | 0
(5) | automatic car washes, i. e. roll-over, |  | 300 * NS / f d | [9 empty] | 2 | 100 | 600 | #DIV/0! | #DIV/0!
| drive-through |  | (c) | [9 empty] | 3 | 200 | 600 | #DIV/0! | #DIV/0!
(a) Not for separators smaller than or equal NS 10, except for covered car parks. | [12 empty] | 4 | 300 | 600 | #DIV/0! | #DIV/0!
(b) Minimum volume of sludge traps 600 l. | [12 empty] | 5 | 300 | 5000 | #DIV/0! | #DIV/0!
(c) Minimum volume of sludge traps 5000 l.
0
0 |  |  |  |  | 0 | [5 empty] | 0 |  |  | #DIV/0!
0 |  |  |  |  | 0 | [8 empty] | #DIV/0!
[5 empty] | 0 | [5 empty] | 0
calculated NS for separators with bypass:
[5 empty] | 0 | [8 empty] | decisive NS for
[5 empty] | 0 | [8 empty] | separators with bypass:
[5 empty] | 0 |  |  |  |  | 0 |  | 0 |  | bypass
FALSE
selected NS for separator
[7 empty] | date: | 2026-07-30 00:52 | [5 empty] | with bypass:
[14 empty] | volume of sludge trap |  | #N/A | l
signature:
[13 empty] | 1 | 0 |  | 0 | 0
[13 empty] | 2 | 100 | 600 | #N/A | #N/A
[13 empty] | 3 | 200 | 600 | #N/A | #N/A
[13 empty] | 4 | 300 | 600 | #N/A | #N/A
[13 empty] | 5 | 300 | 5000 | #N/A | #N/A
Hauraton GmbH & Co KG
Werk Rastatt
Werkstrasse 13
Stand 09/95-11/03. Änderungen vorbehalten. | [6 empty] | D-76437 Rastatt
aquafix, copyright by mathias müller, hameln & roland coerdt, gernsbach | [6 empty] | Telefon +49 /72 22/ 958-0
Telefax +49 /72 22/ 958-100
Marketing@Hauraton.de
WWW.Hauraton.com
ENDE
Instructions for use
to annex B.1 of the norm
table with densities annex A1
The TAB-key brings you to the
next field!
to annex B.2 of the norm

## Tabelle_A1_PD
30
density at 15 to 20 °C (g/cm3) | 0.813
Separability | limited
density factor d for S-I-P | 1
density factor f d for S-II-P | 1
density factor f d for S-I-II-P | 1
maximum solubility | 30 g/l
(under certain conditions)
remarks | 0
0
0
041103
back to calculation

## Tabelle_A1
Annex (informative)
Table A.1 -
density factor f d for particular light liquids and combination of components
|  |  |  | f d |  |  | Remarks
| light liquid | density at 15 to 20 °C (g/cm3) | separability | S-II-P | S-I-P | S-II-I-P | Max. solubility in water under certain conditions | Others
1 | acetic-acid-amylacetate | 0.876 | yes | 2 | 1.5 | 1 | 2,5 g/l | a | a
2 | acetic-acid-ethylester (Ethylaceate) | 0.9 | limited | 3 | 2 | 1 | 86,0 g/l | decomposition in acetic acid and water
3 | acetic-acid-methylacetate | 0,93 to 0,934 | limited | 3 | 2 | 1 | 292 g/l | a particularly in closed compartments | a
4 | acetic-acid-n-butylester | 0.876 | limited | 3 | 1.5 | 1 | 7 g/l | decomposition in acetic acid and ethylalcohol
5 | acetone | 0.791 | no |  |  |  | unlimited
6 | amber oil | 0.8 | yes | 1 | 1 | 1
7 | amylalcohol | 0.815 | limited | 1 | 1 | 1 | 27 g/l | mixtures with water harmful
8 | benzene | 0.87 | yes | 2 | 1.5 | 1 | 1,8 g/l | a | a
9 | butylalcohol | 0.81 | limited | 1 | 1 | 1 | 90 g/l | a | a
10 | coal tar oil | 0,86 to 0,89 | yes | 2 | 1.5 | 1 | 0,2 g/l
11 | cresol oil | 1.03 | no |  |  |  | 20 g/l
12 | cyclohexanol | 0.968 | no |  |  |  | 56,7 g/l
13 | cyclohexane | 0,778 to 0,779 | yes | 1 | 1 | 1 | nearly insoluble | a | a
14 | dekaline (dekahydro-naphtalene) | 0,87 to 0,896 | yes | 2 | 1.5 | 1 | nearly insoluble
15 | diesel fuel, diesel oil | 0.85 | yes | 1 | 1 | 1 | nearly insoluble
16 | diethylether | 0.714 | limited | 1 | 1 | 1 | 75 g/l | emission of diethylether gases
17 | dioxane | 1.036 | no |  |  |  | unlimited | a in case of high concentration | a
18 | ethyl alcohol | 0.789 | no |  |  |  | unlimited | a in case of high concentration | a
19 | ethylbutyrate (butyric-acid-n-ethylester) | 0.879 | limited | 2 | 1.5 | 1 | 6,2 g/l | a | a
20 | ethylmethylketon | 0.805 | no |  |  |  | well soluble
21 | formic acid ethylester | 0,919 to 0,921 | limited | 3 | 2 | 1 | 110 g/l | a | a
22 | formic acid methylester | 0,969 to 0,971 | limited | 3 | 2 | 1 | 300 g/l | a | a
23 | fuel oil, extra light | < 0,86 | yes | 1 | 1 | 1 | nearly insoluble
24 | fuel oil, light | 0.87 | yes | 2 | 1.5 | 1
25 | fuel oil, medium | 0.92 | yes | 3 | 2 | 1
26 | fuel oil, heavy | 0,94 to 0,99 | limited up to 0,96 g/cm3 | 3 | 2 | 1 | nearly insoluble
27 | heavy petrol | 0,7 to 0,75 | yes | 1 | 1 | 1 | nearly insoluble
28 | heptane | 0.684 | yes | 1 | 1 | 1 | nearly insoluble | a | a
29 | hexane | 0.659 | yes | 1 | 1 | 1 | nearly insoluble | a | a
30 | iso-amylalkohol | 0.813 | limited | 1 | 1 | 1 | 30 g/l
31 | iso-butylalcohol | 0.806 | limited | 1 | 1 | 1 | 95 g/l | a on warm days | a
32 | iso-propylalcohol | 0.785 | no |  |  |  | unlimited | a | a
33 | kerosene (jet petrol) | 0.8 | yes | 1 | 1 | 1 |  | a when exposed to sunlight | a
34 | light oil = fuel oil, light | 0.87 | yes | 2 | 1.5 | 1
35 | light petrol = petrol, gasoline | 0,77 to 0,79 | yes | 1 | 1 | 1 |  | a | a
36 | Lignite tar oil = coal tar oil | 0,86 to 0,89 | yes | 2 | 1.5 | 1 | 0,2 g/l
37 | lubricating oil | 0,89 to 0,9 | yes | 2 | 1.5 | 1 | nearly insoluble
38 | methyl alcohol | 0,79 to 0,791 | no |  |  |  | unlimited | a | a
39 | methylcyclohexanol | 0,91 to 0,94 | yes | 3 | 2 | 1
40 | oil of turpentine | 0,86 to 0,87 | yes | 2 | 1.5 | 1 |  | a in case of higher temperatures | a
41 | paraffin oil | 0,88 to 0,94 | yes | 3 | 2 | 1 | nearly insoluble
42 | pentane | 0,625 to 0,626 | yes | 1 | 1 | 1 | 0,36 g/l | a | a
43 | petrol, gasoline, mixture of brands | 0,77 to 0,79 | yes | 1 | 1 | 1 |  | a | a
44 | petrol, gasoline, branded | 0,68 to 0,75 | yes | 1 | 1 | 1 |  | a | a
45 | petrol, racing car | 0.78 | yes, but check formula | 1 | 1 | 1 |  | a | a
46 | petroleum | 0.8 | yes | 1 | 1 | 1 | nearly insoluble | a | a
47 | pine oil = oil of turpentine | 0,86 to 0,87 | yes | 2 | 1.5 | 1 |  | a in case of higher temperatures | a
48 | propionacidethylester | 0,889 to 0,891 | yes | 2 | 1.5 | 1 | 22 g/l | a | a
49 | propylalcohol | 0.804 | no |  |  |  | unlimited
50 | propylbutyrate | 0.88 | yes | 2 | 1.5 | 1 | ~ 0,3 g/l
51 | tetraline (tetrahydronaphthaline) | 0,967 to 0,969 | limited | 3 | 2 | 1
52 | test petrol | 0,764 to 0,794 | yes | 1 | 1 | 1 | nearly insoluble
53 | toluene | 0,866 to 0,867 | yes | 2 | 1.5 | 1 | nearly insoluble | a | a
54 | tractor fuel = diesel fuel and petroleum
55 | transformer oil, not containing PCB | ~0,82 | yes | 1 | 1 | 1
56 | transformer oil, containing PCB | ~0,82 | no
57 | xylene | 0,862 to 0,875 | yes | 2 | 1.5 | 1 | 0,2 g/l | a | a
a = possible formation of explosive atmosphere above water level

## Tabelle_B1
Annexe B (informative)
table B.1 -
list of components and
quality of effluent
direction to flow | configuration | Quality of effluent
a | S-II-P | Recommended as a minimum quality of effluent for input in drainage/sewerage systems and sewage system plants
a | S-I-P | Recommended where higher grade of separation may be required
a | S-II-I-P | Recommended for same quality of effluent as combination S-I-P but where the inflow rate may contain larger quantities of light liquids
a | S-IIb-P | May be used for trapping spillage of light liquid
a | S-Ib-P | May be used for treating the first flush of contaminated run-off
I | class I separator (coalescene)
II | class II separator (oil/petrol separator)
S | sludge trap
P | sampling shaft
b | bypass
051103
back to calculation

## Tabelle_B2
Annex B (informative)
table B.2 - specific cases of application
Treatment before discharge into
| Application | Remarks | P.S. a | S.W.a | Preventive measures
1 | Rainwater from the petrol station | May not contain detergents of cleaning activities | S-II-P | S-I-P | Additional storage capacity for light liquid may be required
2 | Rainwater from oil storage and oil transfer territories |  | S-II-P S-IIbP b | S-I-P
3 | Rainwater from vehicle parks etc. |  | S-II-P S-IIbP b | S-I-P
4 | Rainwater from roads etc. in special cases | e. g. water catchment areas | S-II-P S-IIbP b | S-I-P
5 | Cleaning (spillage and leakage) floors of work-shops, test centres, factories |  |  | Discharge into surface water directly from the separator is not allowed. In very exceptional circumstances and with the agreement of the local authority the discharge into surface water with additional treatment after the separator may be permitted.
5.1 | With use of cleaning agents |  | S-I-P |  | Use of absorbents
5.2 | Without use of cleaning agent |  | S-II-P |  | Collect spills and drains on dry materials.
6 | Vehicle wash |  |  |  | It is advisable to re-use the treated wastewater.
6.1 | By hand | Cleaning only car surfaces, cleansing agents free of hydrocarbons | S-P
6.2 | Automatic car washes | Cleaning only car surfaces, including underwash (low pressure), cleansing agents free of hydrocarbons | S-II-P
6.3 | By high pressure cleaner
6.3.1 | Cleaning only vehicle surfaces without contamination | Cleansing agents free of hydrocarbons | S-P
6.3.2 | Cleaning vehicle surfaces with oil contamination |  | S-I-P C S-II-EBS-P
6.4 | Underwash
6.5 | Engines
6.6 | Self-service by high-pressure cleaner
7 | Cleaning (except car wash) | Cleaning engines or parts | S-I-P S-II-EBS-P S-I-EBS-P
7.1 | With high-pressure cleaner
7.2 | With rotocleaner
8 | Removal of paraffin wax or similar, e. g. from new vehicles, including anti-rost treatment |  | S-II-EBS-P
9 | Scrap yards |  | S-II-P |  | Collect spills and drains on dry materials, to avoid water pollution.
10 | Soil treatment |  | S-II-P
11 | Treatment (plants) for sludge and light liquids from separator |  | S-I-P
a | After treatment the effluent is discharged in a public sewer (P.S.) or in surface water (S.W.). Effluents may be discharged if the quality is conform to the discharge standard required by local authorities
b | Subject to local regulations
c | Conditions: - pressure less than 60 bar - temperature less than 60 ° C - pH-neutral - Using of cleansing agents in accordance with 4.3.2.3 of EN 858
S | sludge trap
I | class I separator
II | class II separator
P | sampling shaft
EBS | emulsion break system or further treatment
041103
back to calculation

## Hinweis
Instruction for use
OK
Abbrechen
The calculation programme for the sizes of separator systems according to EN 858, 10/03, was prepared to the best knowledge and belief. No guarantee can however be given for the accuracy of the calculation.
All rights belong to the author. Copying or changes are not permited.
Suggestions for improvements are gratefully received.
Roland Coerdt
Dipl.-Ing.(FH), M. Eng.
Hofäckerweg 11
76593 Gernsbach
Roland.Coerdt@Hauraton.de