## Startmenue
Selection Grease/fat/oil interceptors according to EN1825 pt 2
Methods based upon the type of establishment discharging into the separator
Hauraton GmbH & Co KG
Werk Rastatt
Werkstrasse 13
D-76437 Rastatt
Telefon +49 /72 22/ 958-0
Telefax +49 /72 22/ 958-100
Revision 05/02, 02/03.modification rights are reserved. | Marketing@Hauraton.de
aquafix, copyright by roland coerdt, gernsbach | WWW.Hauraton.com
Commercial kitchens
Meat processing plants
Calculation based on equipment/fittings discharging into the separator
?
?
?
Densities of greases and oils
Instruction for use

## Zusammenfassung Fleisch
Selection Grease/fat/oil interceptors according to EN1825 pt 2
Meat processing plants
Summary
Meat processing plant |  | #N/A |  | 1 | small, up to 5 GV per week
|  |  |  | 2 | medium, 6 to 10 GV per week
|  |  |  | 3 | large, 11 to 40 GV per week
Peak flow coefficient F: | = | 0
Waste water quantity V (dertermined): | = | 0 | l
Waste water quantity V (calculated): | = | 0 | l
Meat products Mp: | = | 0 | kg
Waste water quantity VP: | = | 0 | l/kg
Production t: | = | 0 | h
Maximum waste water flow QS | = | #DIV/0! | l/s
Density factor fd: | = | 0
Temperature factor ft: | = | 0
Detergent coefficient fr: | = | 0
Norminal Size NS | = | #DIV/0!
Sludge trap volume | = | #DIV/0! | l
0
0
0
0
2026-07-30 00:52
Back

## Zusammenfassung Kueche
Selection Grease/fat/oil interceptors according to EN1825 pt 2
Commercial kitchens
Summary
Appropriate factor |  | #N/A
|  |  |  | 1 | Hotel
|  |  |  | 2 | Restaurant
Peak flow coefficient F: | = | 0 |  | 3 | Hospital
Waste water quantity V (determined): | = | 0 | l | 4 | Factory and office canteens
Waste water quantity V (calculated): | = | 0 | l | 5 | Large catering establishment
Meals per day M: | = | 0 | Pce.
Waste water quantity VM: | = | 0 | l
Production t: | = | 0 | h
Maximum waste water flow QS | = | #DIV/0! | l/s
Density factor fd: | = | 0
Temperature factor ft: | = | 0
Detergent coefficient fr: | = | 0
Norminal size NS | = | #DIV/0!
Sludge trap volume | = | #DIV/0! | l
0
0
0
2026-07-30 00:52
Back

## Dichtefaktor
|  | Faktor fd |  | Dichte g/cm3
|  | 0.4276 |  | 0.85
|  | 0.5 |  | 0.87632
|  | 0.75 |  | 0.91578
|  | 1 |  | 0.94
| 0.4276 | 0.5 | 0.64474 | 0.75 | 1
| 0.85 | 0.87632 | 0.9 | 0.91578 | 0.94
Figure 1 EN 1825-2
Relation between fd and density
Back to calculation meat processing plants
Back to calculation commercial kitchens

## Fleischverarbeitende Betriebe
Selection Grease/fat/oil interceptors according to EN1825 pt 2
Project:
Client:
Designer:
Parameters |  |  |  |  | Input
Meat processing applications
Please select the appropriate factor
from the following list
Meat processing quantity |  |  | Case
small | upto 05 GV each week *) |  | 1 | [9 empty] | 0 | 0
medium | upto 10 GV each week *) |  | 2 | [9 empty] | 0 | 0
large | upto 40 GV each week *) |  | 3 | [9 empty] | 0 | 0
*) 1 GV is a unit equivalent to the processing
of 1 Large Cow or approx 2,5 Pigs |  |  |  | 0 | Case Number: | [7 empty] | 0 | 0
|  |  |  | 0 | 0
Peak flow coefficient F
The factor F is dependand on the throughput
of the processing application
Meat processing plant |  | Peak flow coefficient F
small |  | 30
medium |  | 35
large |  | 40 |  |  | Peak flow coefficient F: |  |  |  |  | = | 0
Waste water quantity V
When you know the average daily
quantity of waste water, please input the value to the right |  |  |  |  | Waste water quantity V: |  |  |  |  | = |  | l
If the waste water quantity is not known please input the daily quantity |  |  |  |  | or
of meat products M, in kg to the right. |  |  |  |  | Meat products Mp: |  |  |  |  | = |  | kg
Factory specific waste water quantity VP
If the waste water quantity V is not known
it is necessary to determine the the waste water quantity Vp
Meat processing |  | Waste water quantity VP
factory |  | l/kg
small | upto 05 GV/week | 20
medium | upto 10 GV/week | 15
large | upto 40 GV/week | 10 |  |  | Waste water quantity VP: |  |  |  |  | = | 0 | l/kg
The average daily waste water quanity V
is determined from the following formula
V = MP * VP |  |  |  |  | V | = | 0 | * | 0 | = | 0 | l
[5 empty] | V determined |  |  |  |  | = | 0 | l
To determine the maximum waste water flow rate QS | [10 empty] | 0
Please input to the right the average daily
production in hours |  |  |  |  | Production t: |  |  |  |  | = |  | h
The maximum waste water flow QS
is determined from the following formula
QS = V * F / (t * 3600) | [6 empty] | 0 | * | 0
[5 empty] | Qs | = | 0 | * | 3600 | = | #DIV/0! | l/s
Density factor fd
Please input the appropriate density to suit your
application to the right from the following list
Density of grease * |  | Density factor fd
upto 0.94 g/cm3 |  | 1
over 0,94 g/cm3 ** |  | 1.5
*) at 20° C
**)valid e.g castor oil, degras, wool grease, resin oil, cattle-tallow |  |  |  |  | Density factor fd: |  |  |  |  | =
Temperature factor ft:
please input to the right for your application
the appropriate solidity factor
Temperature at inlet ° C |  | Temperature factor ft
upto 60 |  | 1
constantly or occasionally > 60 |  | 1.3
[5 empty] | Temperature factor ft: |  |  |  |  | =
Detergent and rinsing agent coefficient fr
please input to the right for your application
the appropriate detergetn or rinsing agent coefficient
Use of detergent |  | Detergent coefficient fr
and rinsing agents
never used |  | 1 | [10 empty] | Hilfstabelle Verhältnis
occasional or constant |  | 1.3 | [10 empty] | 0 | 1
Special use. e.g. hospitals |  | >= 1,5 |  |  | Detergent coefficient fr: |  |  |  |  | = |  |  | 0.01 | 1.3
[13 empty] | 0.751 | 1.5
[13 empty] | 1.51 | 1.7
Calculation of rating nominal size NS
The interceptor rating is determined from the following formula
NS = Qs * fd * ft * fr |  |  |  |  | NS | = | #DIV/0! | * | 0 | * | 0
[6 empty] | * | 0 | * |  | = | #DIV/0!
[5 empty] | Interceptor rating |  |  |  |  | = | #DIV/0!
Calculation of sludge containment volume
The sludge volume should be 200 times the NS | [12 empty] | Hilfstabelle Nenngrößen
rating for meat processing applications |  |  |  |  | Sludge trap volume | [5 empty] | #DIV/0! | l | 0 | 2
[13 empty] | 2.1 | 4
[13 empty] | 4.1 | 7
[13 empty] | 7.1 | 10
[13 empty] | 10.1 | 15
[7 empty] | date: | 2026-07-30 00:52 |  |  |  |  | 15.1 | 20
[13 empty] | 20.1 | 25
[13 empty] | 25.1 | devide
signature:
Hauraton GmbH & Co KG
Werk Rastatt
Werkstrasse 13
D-76437 Rastatt
Revision 05/02.modification rights are reserved. | [5 empty] | Telefon +49 /72 22/ 958-0
aquafix, copyright by roland coerdt, gernsbach | [5 empty] | Telefax +49 /72 22/ 958-100
Marketing@Hauraton.de
WWW.Hauraton.com
END
Back
Aditional Informations
Summary
Density factor from figure 1 EN 1825/2

## Gewerbliche Kuechenbetriebe
Selection Grease/fat/oil interceptors according to EN1825 pt 2
Project:
Client:
Designer:
Parameters |  |  |  | Input
Commercial kitchens
Please select the appropriate factor
from the following list
Commercial kitchens | Case
Hotel | 1 | [10 empty] | 0 | 0
Restaurant | 2 | [10 empty] | 0 | 0
Factory and office canteens | 3 | [10 empty] | 0 | 0
Hospital | 4 | [10 empty] | 0 | 0
Large catering establishment | 5 |  | 0 | 0 | [7 empty] | 0 | 0
(24 h operation) |  |  |  | Case Number: | [7 empty] | 0 | 0
Peak flow coefficient F
The factor F is dependand on the condition
of the processing application
Commercial kitchens | Peak flow coefficient F
Hotel | 5
Restaurant | 8.5
Factory and office canteens | 20
Hospital | 13
Large catering establishment | 22 |  |  | Coefficient F: |  |  |  |  | = | 0
(24 h operation)
Waste water quantity V
When you know the average daily
quantity of waste water, please input the value to the right |  |  |  | Waste water quantity V: |  |  |  |  | = |  | l
If the waste water quantity is not known please input the daily quantity |  |  |  | or
of meals M, to the right. |  |  |  | Meals per day M: |  |  |  |  | = |  | pce.
Kitchen specific waste water quantity VM
If the waste water quantity V is not known
it is necessary to determine the the waste water quantity Vm
Commercial kitchens | Waste water quantity VM
Hotel | 100
Restaurant | 50
Factory and office canteens | 5
Hospital | 20
Large catering establishment | 10 |  |  | Waste water quantity VM: |  |  |  |  | = | 0 | l
The average daily waste water quanity V
is determined from the following formula
V = M * VM |  |  |  | V | = | 0 | * | 0 | = | 0 | l
|  |  |  | V determined |  |  |  |  | = | 0 | l |  | 0
0
To determine the maximum waste water flow rate QS | [9 empty] | 0 |  |  | 0
0
Please input to the right the average daily
production in hours |  |  |  | Production t: |  |  |  |  | = |  | h
The maximum waste water flow QS
is determined from the following formula
QS = V * F / (t * 3600) | [5 empty] | 0 | * | 0
|  |  |  | Qs | = | 0 | * | 3600 | = | #DIV/0! | l/s
Density factor fd
Please input the appropriate density to suit your
application to the right from the following list
Density of grease * | Density factor fd
upto 0.94 g/cm3 | 1
over 0,94 g/cm3 ** | 1.5
*) at 20° C
**)valid e.g castor oil, degras, wool grease, resin oil, cattle-tallow |  |  |  | Density factor fd: |  |  |  |  | =
Temperature factor ft:
please input to the right for your application
the appropriate solidity factor
Temperature at inlet ° C | Temperature factor ft
upto 60 | 1
constantly or occasionally > 60 | 1.3 |  |  | Temperature factor ft: |  |  |  |  | =
Detergent and rinsing agent coefficient fr
please input to the right for your application
the appropriate detergetn or rinsing agent coefficient
Use of detergent | Detergent coefficient fr
and rinsing agents
never used | 1 | [10 empty] | Hilfstabelle Verhältnis
occasional or constant | 1.3 | [10 empty] | 0 | 1
Special use. e.g. hospitals | >= 1,5 |  |  | Detergent coefficient fr: |  |  |  |  | = |  |  | 0.01 | 1.3
Calculation of rating nominal size NS | [11 empty] | 0.751 | 1.5
[12 empty] | 1.51 | 1.7
The interceptor rating is determined from the following formula | [11 empty] | 0.751 | 1.5
[12 empty] | 1.51 | 1.7
NS = Qs * fd * ft * fr |  |  |  | NS | = | #DIV/0! | * | 0 | * | 0
[5 empty] | * | 0 |  |  | = | #DIV/0!
|  |  |  | Intercepotor rating |  |  |  |  | = | #DIV/0!
Calculation of sludge containment volume
The sludge volume should be 100 times the NS | [11 empty] | Hilfstabelle Nenngrößen
rating for commercial kitchens. |  |  |  | Sludge trap volume | [5 empty] | #DIV/0! | l | 0 | 0
[12 empty] | 1e-05 | 2
[12 empty] | 2.1 | 4
[12 empty] | 4.1 | 7
[12 empty] | 7.1 | 10
[6 empty] | date: | 2026-07-30 00:52 |  |  |  |  | 10.1 | 15
[12 empty] | 15.1 | 20
[12 empty] | 20.1 | 25
[6 empty] | signature: | [5 empty] | 25.1 | devide
Hauraton GmbH & Co KG
Werk Rastatt
Werkstrasse 13
D-76437 Rastatt
Telefon +49 /72 22/ 958-0
Revision 05/02.modification rights are reserved. |  |  |  |  | Telefax +49 /72 22/ 958-100
aquafix, copyright by roland coerdt, gernsbach |  |  |  |  | Marketing@Hauraton.de
WWW.Hauraton.com
END
Back
Summary
Density factor from figute 1 EN 1825/2

## Summation
Selection Grease/fat/oil interceptors according to EN1825 pt 2
Project:
Client:
Designer:
Parameters | [6 empty] | Input
Calculation based on equipment/fittings discharging into the separator
Values of qi and Zi(n) for typical fittings/equipment
Please fill out number of fittings/equipment.
Type of kitchen equipment |  |  | m | qi (l/s) | Zi (n) | [7 empty] | Number
Boliling pan 25 mm outlet |  |  | 1 | 1 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
Boiling pan 50 mm outlet |  |  | 2 | 2 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tilting boiling pan 70 mm outlet |  |  | 3 | 1 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tilting boiling pan 100 mm outlet |  |  | 4 | 3 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rinse sink 40 mm siphon outlet |  |  | 5 | 0.8 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rinse sink 50 mm siphon outlet |  |  | 6 | 1.5 | 0 | 0 | 0 | [6 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rinse sink 40 mm non-siphonic |  |  | 7 | 2.5 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rinse sink 50 mm non-siphonic |  |  | 8 | 4 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dish washer |  |  | 9 | 2 | 0 | [7 empty] | 0 | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tiltin roasting tin |  |  | 10 | 1 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fixed roasting tin |  |  | 11 | 0.1 | 0 | [7 empty] | 0 | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
High pressure or steam cleaner |  |  | 12 | 2 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scraper |  |  | 13 | 1.5 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetable washer |  |  | 14 | 2 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Values of qi and Zi(n) for draw-of-points
Where two or more draw-off points are installed only for washing down purposes
but are not connected to any quipment, their flow rate should be calculated
using the equation and this table.
Size of draw-off points |  |  | m | qi (l/s) | Zi (n) | [7 empty] | Number
DN 15 | R ½ |  | 15 | 0.5 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
DN 20 | R ¾ |  | 16 | 1 | 0 | [8 empty] | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
DN 25 | R 1 |  | 17 | 1.7 | 0 | [7 empty] | 0 | pce. | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Manufacturer´s values should be used, if different to those given in this table.
For equipment and fittings not listet in this tables values of qi and Zi(n) should
be determined by testing or by reference to manufacturer´s data.
Maximum waste water flow Qs
The maximum wastewater flow rate QS
is calculated from the eqation:
j (n)
Qs = S [(n * qi * Zi (n)] | [10 empty] | Qs | = | 0 | l/s
i = 1
Qs = is the maximum wastewater flow in l/s
j = is the dimensionless counter | [11 empty] | = | 0 | m3/d
m = is the reference number of fittings and piecec of equipment, dimensonless
n = is the number of fittings/equipment of the same type, dimensionless
Qi = is the maximum discharge from fittings/equipment in l/s
Zi (n) = is the frequency factor, dimensionless
Density factor fd
Please input the appropriate density to suit your
application to the right from the following list
Density of grease * |  | Density factor fd
upto 0.94 g/cm3 |  | 1
over 0,94 g/cm3 ** |  | 1.5
*) at 20° C
**)valid e.g castor oil, degras, wool grease, resin oil, cattle-tallow | [6 empty] | Density factor fd: |  |  |  |  | =
Temperature factor ft:
please input to the right for your application
the appropriate solidity factor
Temperature at inlet ° C |  | Temperature factor ft
upto 60 |  | 1
constantly or occasionally > 60 |  | 1.3 |  |  |  |  | Temperature factor ft: |  |  |  |  | =
Detergent and rinsing agent coefficient fr
please input to the right for your application
the appropriate detergetn or rinsing agent coefficient
Use of detergent |  | Detergent coefficient fr
and rinsing agents
never used |  | 1
occasional or constant |  | 1.3
Special use. e.g. hospitals |  | >= 1,5 |  |  |  |  | Detergent coefficient fr: |  |  |  |  | =
Calculation of rating nominal size NS
The interceptor rating is determined from the following formula
NG = Qs * fd * ft * fr | [6 empty] | NS | = | 0 | * | 0 | * | 0
[8 empty] | * | 0 |  |  | = | 0
[7 empty] | Interceptor rating |  |  |  |  | = | 0
Calculation of sludge containment volume | [6 empty] | Commercial kitchen k | [7 empty] | 0
[7 empty] | Meat processing application m | [7 empty] | 0
The sludge volume should be 100 times the NS rating for | [14 empty] | 0
commercial kitchens and 200 times the NS rating for | [6 empty] | Sludge trap volume | [5 empty] | 0 | l
meat processing applications.
Hilfstabelle Nenngrößen
[9 empty] | date: | 2026-07-30 |  |  |  |  | 0 | 0
[15 empty] | 1e-05 | 2
[15 empty] | 2.1 | 4
[9 empty] | signature: | [5 empty] | 4.1 | 7
[15 empty] | 7.1 | 10
[15 empty] | 10.1 | 15
[15 empty] | 15.1 | 20
[6 empty] | Hauraton GmbH & Co KG | [8 empty] | 20.1 | 25
[6 empty] | Werk Rastatt | [8 empty] | 25.1 | devide
Werkstrasse 13
D-76437 Rastatt
Revision 05/02.modification rights are reserved. | [5 empty] | Telefon +49 /72 22/ 958-0
aquafix, copyright by roland coerdt, gernsbach | [5 empty] | Telefax +49 /72 22/ 958-100
Marketing@Hauraton.de
WWW.Hauraton.com
END
Back

## Dichtetabelle
Densities of greases and oils
Table B.1 EN 1825-2
Fat/Oil | Density r at temperature of 20 °C g/cm3
Animal fat | 0,85 to 0,94
Aniseseed oil | 1,00
Butter fat | 0,91
Cacao butter | 0,89 to 0,94
Castor oil | 0,95 to 0,97*
Coconut oil | 0,92 to 0,93
Corn oil | 0,92
Cottonseed oil | 0,92
Pine oil | 0,87 to 0,91
Fish oil | 0,89 to 0,94
Jojoba oil | 0,86 to 0,90
Lard oil | 0,91 to 0,92
Linseed oil | 0,93 to 0,94
Majoram oil | 0,89 to 0,91
Oleic acid | 0,89 to 0,90
Olive oil | 0,91
Palmitic oil | 0,84
Palmkernel oil | 0,94 to 0,95
Palm oil | 0,91 to 0,92
Peanut oil | 0,91 to 0,92
Pine oil | 0,93 to 0,94
Poppy oil | 0,92
Rapeseed oil | 0,91 to 0,92
Resin oil | 0,87 to 0,91
Sesame oil | 0,92
Soybean oil | 0,92 to 0,93
Stearic acid | 0,84
Sunflower oil | 0,92 to 0,93
Tallow | 0,92
Vegetable oil | 0,95 to 0,97*
Wood oil | 0,95 to 0,97*
*Specific attention shall be given if fat/oil is treated in grease separator according to EN 1825-2
Back

## Dialog1
Hauraton GmbH & Co KG
Selection of norminal size
Oil/fat/grease interceptors
In the case of meat processing by hand the quantity of meat products per day may be assumed to be approximately Mp* 100 kg/GV. Additional wastewater volume per day from e.g. party services, food/snack distributation shall be added when calculating the average waste water quantity V.
OK

## Dialog2
Hauraton GmbH & Co KG
Selection of norminal size
Oil/fat/grease interceptors
The program calculates the capacity of separators according to EN 1825-2, 05/02 - Commercial kitchens.
Theese are e.g. hotels, restaurants, factory and office canteens, hospitals or lage catering establishments.
Method based upon the type of establishment discharging into the separator.
OK

## Dialog3
Hauraton GmbH & Co KG
Selection of norminal size
Oil/fat/grease interceptors
The program calculates the capacity of separators according to EN 1825-2, 05/02 - Meat processing plants and butchers.
Method based upon the type of stablishment discharging into the separator.
OK

## Dialog4
Hauraton GmbH & Co KG
Selection of norminal size
Oil/fat/grease interceptors
The program calculates the capacity of separators according to EN 1825-2, 05/02 - Commercial kitchens.
Theese are e.g. hotels, restaurants, factory and office canteens, hospitals or lage catering establishments.
Calculation based on equipment/fittings discharging into the separator.
OK

## Dialog5
Hinweise zur Benutzung
The program to calculate capacity of separators according to EN 1825-2, 05/02 has been prepared with the best and intent and knowledge. No guarantee can however be given for the accuracy of the calculation.
All rights belong to the author, copying or changes are not permited.
Suggestions for improvements are gratefully received.
OK
Abbrechen
Roland Coerdt
Dipl.-Ing.(FH), M. Eng.
Hofäckerweg 11
D-76593 Gernsbach
Roland.Coerdt@Hauraton.de